TEMPERATURE CONTOLLER SCREEN
←    	ɷ    		↑    	↓
Set    	Advance	Up	Down

Press/ Hold ←       		for 3 seconds and release
				CnPt / J1
Press ɷ 			tpun / F (Fahrenheit or Celsius)
Press ɷ 			tp-H / 165
Press ɷ 			tp-L / 50
Press ɷ 			CtrL / onoF
Press ɷ 			S-HC / Heat
Press ɷ 			ALA1 / 12
Press ɷ 			ALA2 / 0
Press ɷ 			C-SL / ASC11
Press ɷ 			CoSH / oFF
Press ɷ 			C-no / 1
Press ɷ 			bps / 9600
Press ɷ 			Len / 7
Press ɷ 			PrtY / EvEn
Press ɷ 			Stop / 1

Press ←     			
				r-5 / ruN
Press ɷ 			AL1H / 0
Press ɷ 			AL1L / 0
Press ɷ 			Loc / off *
Press ɷ			Displays Temp/Set Point
*Change off to 2 and press ← 

CHANGING HYSTERISYS (Temperature bandwidth)
Press ←   			HGS/ 5
[bookmark: _GoBack] Press ɷ			tp.of/ 0.0  (Adjust to change calibration offset)	

CHANGING HIGH LIMIT TEMPERATURE SETTING
Press/ Hold ←    ɷ simultaneously for 3 seconds
Screen blinks once
Press/ Hold ← for 3 seconds
CnPt / J1 appears
Press ɷ	
Press ɷ
Press ↑ to desired high limit set point
Press ←
Press ←
SETTING LOCK MODE
Press ɷ (4 times) until Loc / Off




All parameter changes are accomplished with the UP and DOWN arrow keys.
All Changes must be set into memory with the SET key (←)


